## PHE
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for PHE and associated works
Sl. No | Description of Work | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount (Rs.)
1 | Constructing brick masonry chamber for underground C.I. inspection chamber and bends with bricks in cement mortar 1:4 (1 cement : 4 coarse sand) C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover with frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg), R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 fine sand : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand), finished smooth with a floating coat of neat cement on walls and bed concrete etc. complete as per standard design:(Only Excess STP Water connecting to Out side ) | EACH | 4 |  |  | 0
2 | Supplying and fixing of SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 6 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. |  |  |  |  | 0
a | 75mm dia (Internal ) | RM | 330 |  |  | 0
b | 75mm dia (ASP) | RM | 112 |  |  | 0
c | 110mm dia (Internal ) | RM | 230 |  |  | 0
d | 75mm dia (DTP) | RM | 250 |  |  | 0
e | 110mm dia (DTP ) | RM | 35 |  |  | 0
f | 125mm dia (DTP) | RM | 140 |  |  | 0
3 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings and fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc |  |  |  |  | 0
| DOMESTIC WATER SUPPLY |  |  |  |  | 0
a | 15.90mm OD pipe | RM | 240 |  |  | 0
b | 22.20mm OD pipe | RM | 150 |  |  | 0
c | 28.60mm OD pipe | RM | 80 |  |  | 0
d | 34.90mm OD pipe | RM | 0 |  |  | 0
4 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. |  |  |  |  | 0
a | 41.30mm OD pipe | RM | 216 |  |  | 0
| FLUSH WATER SUPPLY |  |  |  |  | 0
a | 15.90mm OD pipe | RM | 180 |  |  | 0
b | 22.20mm OD pipe | RM | 150 |  |  | 0
c | 28.60mm OD pipe | RM | 40 |  |  | 0
d | 34.90mm OD pipe | RM | 0 |  |  | 0
| Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. |  |  |  |  | 0
a | 41.30mm OD pipe | RM | 150 |  |  | 0
| KITCHEN |  |  |  |  | 0
a | 15.90mm OD pipe | RM | 40 |  |  | 0
b | 22.20mm OD pipe | RM | 60 |  |  | 0
5 | Supply and fixing of UPVC Pipes and Fittings SCH-40 Grade to meet the requirement of ASTM-D 2846 for hot and cold water (IS 15778:2007) including cost and conveyance of all materials to site, labour charges for fixing, overheads & contractors profit complete for finished item of work at all floor levels. |  |  |  |  | 0
| DOMESTIC WATER SUPPLY |  |  |  |  | 0
a | 65mm OD pipe | RM | 90 |  |  | 0
b | 80mm OD pipe | RM | 200 |  |  | 0
c | 100mm OD pipe | RM | 82 |  |  | 0
| FLUSH WATER SUPPLY |  |  |  |  | 0
a | 65mm OD pipe | RM | 80 |  |  | 0
b | 80mm OD pipe | RM | 80 |  |  | 0
c | 100mm OD pipe | RM | 30 |  |  | 0
| TERRACE TANK FILLING |  |  |  |  | 0
a | 80mm OD pipe | RM | 80 |  |  | 0
| TERRACE DOMESTIC |  |  |  |  | 0
a | 65mm OD pipe (AIR VENT) | RM | 20 |  |  | 0
b | 80mm OD pipe | RM | 60 |  |  | 0
| TERRACE FLUSH |  |  |  |  | 0
a | 65mm OD pipe (AIR VENT) | RM | 20 |  |  | 0
b | 80mm OD pipe | RM | 60 |  |  | 0
6 | Providing and fixing M.S fabricated hot dipped galvinised coating puddle flange comprising of 600 mm dia long M.S class 'B' pipe (screwed end up to 50 mm & flange for more than 50 mm dia) with 6 mm thick M.S plates of required size including cutting holes in centre of plate, inserting pipe & making welded (Arc) joint complete. Same shall be installed with TEC welded joint in position with reinforcement bars of RCC tank wall/slab including making cutout in shuttering during concrete casting of tank of following diameter. (Location: underground/ overhead tanks.) |  |  |  |  | 0
a | 100 mm OHWT Fire Fighting | EACH | 4 |  |  | 0
b | 65 mm OHWT | EACH | 4 |  |  | 0
7 | Fixing water meter and stop cock in G.I. pipe line including cutting and threading the pipe and making long screws etc. complete (cost of water meter and stop cock to be paid separately). | EACH | 15 |  |  | 0
8 | Providing and fixing C.I. sluice valves (with cap) complete with bolts, nuts, rubber insertions etc. (the tail pieces if required will be paid separately) : | EACH | 2 |  |  | 0
9 | Providing, installing, testing and commissioning of ‘Dewatering Submersible Sump Pump’ with its capacity as 150 LPM at 15 m head, (1 No. Duty + 1 No. Standby) including level probes and all necessary electrical panel with electrical work between Pump and electrical panel complete. Pump to be fully submersible type and to be on Auto operation. Panel to be complete with ammeters, voltmeters, automatic alternating, indicating lamp for pump on / off, pump fault indicator, single phase preventer cum overload relay, low level cut off. Auto / manual mode, selector switches etc. complete. Panel to be earthed | NO | 2 |  |  | 0
10 | Providing & fixing C.I. `Y' Strainer (screwed / flanged) with stainless steel fine wire mesh perforated sheet basket with necessary flange / unions nuts, bolts and washers complete as required. | NO | 2 |  |  | 0
11 | Construction of brick masonry support for GI pipe of size 304.80mm x 228.60mm x 228.60 mm in CM (1:8) prop including plastering and finishing with 12mm thick in CM (1:5) including cost and conveyance of all materials and all labour charges, overheads & contractors profit complete for finished item of work for all floors. | EACH | 20 |  |  | 0
12 | Supply, Installation, Testing & Commissioning of complete composite hydropneumatic system consisting of horizontal /vertical multistage centrifugal pump having stainless steel SS-304 stage casing and SS 304 impellers with stainless steel SS-304 shaft as per IEC standards and GJL250 cast iron suction & discharge casing with single mechanical seal and pressurised tank of suitable capacity as per manufacturer calculation, complete with all standard accessories including pressure switch, pressure gauges, non-return & isolating valves on suction and delivery side with nuts, bolts & washer including mild steel flanges, where ever required with 3 mm thick rubber insertion, with necessary protection and operational devices i.e alternate pumping operation and shut-off during dry running conditions etc. with suitable electrical motor to be operated on 210/220 OR 400/440 volt 50 cycle AC supply, suitable for following duty and with total no. of pumps - 2 nos.(1 working+1standby) complete with Control Unit Panel, manifolds & chassis, as per the approval of Project-in-charge complete complete with M.S fabricated base frame, nuts and bolts bolted to cement concrete foundations complete as per requirement. , 200 LPM HDPE Tank , Panel it including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work.(1 Working +1 Stand by) Head 65.00 m & Discharge 7.00 l/sec | NO | 2 |  |  | 0
13 | Supply, Installation, Testing & Commissioning of complete composite hydropneumatic system consisting of horizontal /vertical multistage centrifugal pump having stainless steel SS-304 stage casing and SS 304 impellers with stainless steel SS-304 shaft as per IEC standards and GJL250 cast iron suction & discharge casing with single mechanical seal and pressurised tank of suitable capacity as per manufacturer calculation, complete with all standard accessories including pressure switch, pressure gauges, non-return & isolating valves on suction and delivery side with nuts, bolts & washer including mild steel flanges, where ever required with 3 mm thick rubber insertion, with necessary protection and operational devices i.e alternate pumping operation and shut-off during dry running conditions etc. with suitable electrical motor to be operated on 210/220 OR 400/440 volt 50 cycle AC supply, suitable for following duty and with total no. of pumps - 2 nos.(1 working+1standby) complete with Control Unit Panel, manifolds & chassis, as per the approval of Project-in-charge complete complete with M.S fabricated base frame, nuts and bolts bolted to cement concrete foundations complete as per requirement. , 200 LPM HDPE Tank , Panel it including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work.(1 Working +1 Stand by)Head 65.00 m & Discharge 7.00 l/sec | NO | 2 |  |  | 0
14 | Supply and fixing, testing and commissioning of Domestic Pumps including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work.(1 Working +1 Stand by) | NO | 2 |  |  | 0
15 | Supply and fixing, testing and commissioning of Flush water Pumps including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work.(1 Working +1 Stand by) | NO | 2 |  |  | 0
16 | Providing and fixing C.I. double acting air valve of approved quality with bolts, nuts, rubber insertions etc. complete (The tail pieces, tapers etc if required will be paid separately) | EACH | 2 |  |  | 0
17 | Providing and fixing PTMT Ball cock of approved quality, colour and make complete with Epoxy coated aluminium rod with L.P./ H.P.H.D. plastic ball | EACH | 8 |  |  | 0
18 | Providing and laying S&S Centrifugally Cast (Spun) / Ductile Iron Pipes conforming to IS : 8329 : | EACH | 200 |  |  | 0
19 | Providing & fixing heavy duty tested ISI marked Pressure Reducing Value (P.R.V) of approved quality For 80 mm Dia | EACH | 2 |  |  | 0
20 | Providing & fixing heavy duty tested ISI marked Pressure Reducing Value (P.R.V) of approved quality For 65 mm Dia | EACH | 4 |  |  | 0
21 | Providing and fixing C.P. brass long nose bib cock of approved quality conforming to IS standards and weighing not less than 810 gms | EACH | 4 |  |  | 0
22 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. | EACH | 0 |  |  | 0
23 | Supplying and fixing of SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 8Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. For 200 mm Diameter | RM | 60 |  |  | 0
| RAIN WATER PIES |  |  |  |  | 0
24 | Providing and fixing on wall face unplaqsticised- PVC rain water pipes confirming to IS: 13592 TYPE A, including jointing with seal ring confirming to IS: 5382 leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. 75mm diameter. |  |  |  |  | 0
a | 125 MM DIA | RM | 360 |  |  | 0
b | 160 MM DIA | RM | 200 |  |  | 0
25 | Providing and fixing on wall face unplaqsticised- PVC moulded fitting/ accessories for unplaqsticised- PVC rain water pipes confirming to IS: 13592 TYPE A, including jointing with seal ring confirming to IS: 5382 leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. Single Tee with door 160x160x160 ,mm |  |  |  |  | 0
0
a | Bend 87.5 degree 160 mm bend | EACH | 20 |  |  | 0
26 | Making khurras 45x45 cm. with average minimum thickness of 5 cm cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) over PVC sheet1mx1mx400 micron, finished with12 mm cement plaster1:3 (1 cement : 3 coarse sand) and a coat of neat cement, rounding the edges and making and finishing the outlet complete) | EACH | 20 |  |  | 0
27 | Supplying and fixing of SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 8Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. For 250 mm Diameter | RM | 100 |  |  | 0
28 | Manufacture, supply and delivery of DI (Ductile Iron) Wafer Butterfly valves conforming to IS 13095 (and its amendments). With hand lever below 150 mm, with Worm gear for 200 mm and above | NOS | 4 |  |  | 0
29 | Supply, installation, testing and commissioning of C.I. non - return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc as required Makes: Audco / Kirloskar / BDK / HShankar / Leader/ Zolotto / Intervalve / Honeywell./ Kartar | NOS | 8 |  |  | 0
30 | Supply, Transportation and Installation of hot dip GI perforated cable tray without cover along with coupler plates, T's, Bends, Reducers, Anchor bolts, nuts, washers and slotted channels / Angle Iron Channels etc complete and the tray should be fitted on the wall / Ceiling etc. complete for finished item of work. (Makes: DEC/MNR/ H FAB or equivalent) | RM | 200 |  |  | 0
31 | Supplying and fixing Gunmetal Gate ( GM peet ) valve as per IS-778 Class - I , Indian make heavy type including cost and conveyance of all materials , labour charges , overheads & contractors profit complete for finished item of work. |  |  |  |  | 0
a | 20 mm Dia. | EACH | 156 |  |  | 0
32 | Terrace Floor |  |  |  |  | 0
a | 80mm Nominal bore | EACH | 10 |  |  | 0
33 | Providing, Fixing, Testing & Commissioning of nitrle rubber insulation on hot water supply pipes. K-Flex, A-Flex, Armacell 15mm (9 mm thickness) |  |  |  |  | 0
a | 20mm (9 mm thickness) | RM | 30 |  |  | 0
b | 25mm dia (9 mm thickness) | RM | 20 |  |  | 0
34 | For Water level indicators with following details: Underground tanks Minimum 4 level Multi level indicators with magnetic type sensor probes complete | EACH | 2 |  |  | 0
35 | Overhead tanks Minimum 4 level Multi level indicators with magnetic type sensor probes complete | EACH | 2 |  |  | 0
36 | Providing, fixing and testing of factory fitted packaged type skid mounted pumping system comprising of :- Horizontal inline centrifugal pumping set with CI casing and SS-304 impellers with stainless steel SS-316L shaft as per IEC standards and GJL250 cast iron suction & discharge casing, connected to TEFC ventilated induction motor of 2 pole, 2900rpm, suitable for 400/440 Volts, 3 phase, 50 Hz A.C. supply. Motor Control Panel with DOL starter MCB and controller for cyclic operation of pumps. Pump working sequence should change after every operation. Contractor overload relays and MCBs should confirm to IEC 898 – 1995/ specifications. Blinking indications for pumps start, trip, low level trip, health supply should be provided in the panel along with the ammeter & voltmeter. Control panel should also consist of cooling fan and liquid level controller with control wiring from UG tank to UG tank with float switch for controlling cut-off and cut-in of pumps and dry run protection complete in all respects. Suction and delivery header with Ball valves Hot Pressed brass OT-58 with stainless steel ball and P.T.F.E seal and O-Ring. NRVs to be used should be with Springs and O-Ring arrangement. Complete set system to be mounted on a common base frame and shall follow following duty. Filter Feed Pump No. of Pumps: 2(1Working + 1 Stand by ) Capacity : 450 lpm Head : 20m | SET | 1 |  |  | 0
37 | Providing and fixing vertical pressure filter with dual media filter (comprising of 600mm bed depth of graded sand gravel and 600mm bed depth of Anthracite) fabricated from high performance M.S plate of minimum 8mm thick for shell & 10mm thick for dished ends with top and bottom flanged openings including top and bottom hub and lateral distribution and collection system complete with initial charge of filter media, face piping, valves, accessories, painting, testing and commissioning complete.(Tested to 6 Kg/m2) Discharge : 450 lpm Filtration Rate : 15000 lit./m2/h Suggested dia app. : 1.60 m | EACH | 1 |  |  | 0
38 | Activated carbon Filter (Domestic Water) Providing and fixing vertical activated carbon filter comprising of activated carbon filter media fabricated from high performance M.S plate of minimum 8mm thick for shell & 10mm thick for dished ends with top and bottom flanged openings including top and bottom hub and lateral distribution and collection system complete with initial charge of filter media, face piping, valves, accessories, Epoxy painting, testing and commissioning complete.(Tested to 6 Kg/m2) Discharge : 450 lpm Filtration Rate : 15000 lit./m2/h Suggested dia app. : 1.60 m | EACH | 1 |  |  | 0
39 | Providing, fixing, testing & commissioning of MSEP water softening plant (suitable for 3 Kg/Sqcm working pressure) complete with initial charge with T-40 NA Resin, multiport valve with built in ejector for controlling all operations), regeneration system and HDPE tank, pressure gauge at inlet, outlet and back wash (each with isolation cock), valves, fittings and water hardness testing kit & associated works. Softener shall be suitable for the following duty: Note: The successful contractor will have to carry out a test of raw water from all the sources of water for the Commercial, Residential & apartment at their own cost from a reputed lab as approved by the Engineer-in-Charge / Consultant. On the basis of these results the contractor has to submit his shop drawings, design calculations and specifications accordingly. Please note that it is ultimately the responsibility of the contractor to provide treated water for different use as per International Standard as given in the attached guidelines. Raw water hardness 500 Mg/L Treated water hardness 100 Mg/L Regeneration Period 12 Hrs. Capacity : 700 lpm | SET | 1 |  |  | 0
40 | Supplying, installing, testing and commissioning of dosing system (for domestic water treatment plant) consisting of one HDPE tank of 100 litres capacity with a positive displacement diphragm dosing pump having variable flow rate of 0-6 lph. The motor shall be suitable for operation at 240 V / single phase/50 Hz. Supply. The pump shall be supplied complete with necessary polypropylene piping, valves, strainers, low level switch and injection fittings. The pump shall be speed & stroke control Asia LMI / equivalent make. The cost shall be inclusive of providing salt for the testing and operation of system before handover to the owner | SET | 1 |  |  | 0
41 | Supplying, installing, testing and commissioning of annunciation and indication panel with interlocking arrangement complete in accordance to specification for level controller etc with control cabling from field to MCC as required. The system shall be complete to ensure automatic operation of pump in accordance to water level in respective tanks. | EACH | 1 |  |  | 0
42 | Providing & fixing level controllers for water pumps to start/stop the pump at set level. Including wiring, cabling from pump to panel & all other accessories as required to operate the system automatically. | EACH | 1 |  |  | 0
43 | Providing & fixing pressure switch for water pumps to start/stop the filter feed pump at set pressure. Including wiring, cabling from pump to panel & all other accessories as required to operate the system automatically. | EACH | 4 |  |  | 0
44 | Supply, installation, testing and commissioning of tanker inlet connection complete with 200 mm dia GI (heavy) inlet piping, hose inlet connection, MS cabinet enclosure (epoxy painted after fabrication), pad locking arrangement, inlet flexible hose complete with all necessary arrangement | EACH | 1 |  |  | 0
45 | Providing & fixing butterfly valve Rated for PN16 pressure rating. Including rubber gasket, flanges, nuts, bolts, washers & painting complete as required. 50 mm dia |  |  |  |  | 0
| 100 mm dia | EACH | 4 |  |  | 0
46 | Providing & fixing CI `Y' Strainer (screwed/ flanged) with stainless steel fine wire mesh perforated sheet basket with necessary flange/ unions nuts, bolts and washers complete as required (on pump suction). | EACH | 2 |  |  | 0
66 | Supply, Installation, Testing and Commissioning of water softener of flow rate as mentioned with FRP pressure vessel of approved make as per specification with high exchange capacity strongly acidic cation exchange resin, stainer system, distribution, collection system, multiport valve for operation with pressure gauge at inlet, outlet and other standard accessories like foundation bolts, piping for inlet, outlet and backwash complete. The filter unit shall be provided with a bypass system in order to isolate it from the treatment line. The cost of piping upto the inlet of the soft water sump is included in the item of work complete as per specifications and direction of Engineer-In-Charge. Pressure rating of vessel in bars - 10bar Feed water hardness (CaCO3) - 500PPM Expected output water hardness (CaCO3) - 50PPM Volume of water to be processed in litres per day -155,000lts. Quantity of resin in litres - 1465lts Flow rate - 17.51 Size of vessel in inches - 48" x 72" Multi port valve size in mm - 65mm dia Diameter of Rotameter on softener inlet in mm - 65mm dia | Set | 2 |  |  | 0
67 | Supply, Installation, Testing and Commissioning of Pressure Sand Filter of flow rate as mentioned with FRP pressure vessel of approved make as per specification with high quality filter grade media, distribution, collection system with strainer, multiport valve for operation with pressure gauge at inlet, outlet and other standard accessories like foundation bolts, CPVC piping for inlet, outlet and backwash complete. The filter unit shall be provided with a isolation valve on inlet, axial flow reflux valve on outlet, bypass valve on the interconnection between inlet and outlet of required size for pipes in order to isolate it from the treatment line. The cost of piping upto the outlet of the softener inlet is included in the item of work complete as per specifications and direction of Engineer-In-Charge. Pressure rating of vessel in bars - 10bar Flow rate - 17.51m3/ hr Size of vessel in inches - 48" x 72" Multi port valve size in mm - 65mm dia Quantity of filter media in kgs - 1868kgs. Valve on inlet pipe in mm - 62.50mm dia Diameter of Rotameter on filter inlet in mm - 65mm dia | Set | 2
| TOTAL C/O SUMMARY |  |  |  |  | 0

## Additional items
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for Additional items - PHE
Sl.No. | Description | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount
0
1 | [5 empty] | 0
2 | [5 empty] | 0
3 | [5 empty] | 0
4 | [5 empty] | 0
5 | [5 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| TOTAL C/O SUMMARY |  |  |  |  | 0