## STP
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for STP and associated works
Sl.No. | Description | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount (Rs.)
I | MECHANICAL WORKS
1 | Supply and fixing, testing and commissioning of Manual Coarse Bar Screen | No. | 1 |  |  | 0
| Size: To Suit 400mm Wide x 200mm Liquid Height |  |  |  |  | 0
| Clear Opening of Screen: 25mm |  |  |  |  | 0
| Size of Flat: 50mm x 6mm |  |  |  |  | 0
| Angle of Inclination: 60 Degree |  |  |  |  | 0
| Shape of Screen: Curved Top |  |  |  |  | 0
| Accessories: Rake & 2 Nos. Side Plate |  |  |  |  | 0
| MOC: SS 304 |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
2 | Supply and fixing, testing and commissioning of Manual Fine Bar Screen | No. | 1 |  |  | 0
| Size: To Suit 300mm Wide x 200mm Liquid Height |  |  |  |  | 0
| Clear Opening of Screen: 10mm |  |  |  |  | 0
| Size of Flat: 50mm x 6mm |  |  |  |  | 0
| Angle of Inclination: 45 Degree |  |  |  |  | 0
| Shape of Screen: Curved Top |  |  |  |  | 0
| Accessories: Rake |  |  |  |  | 0
| MOC: SS 304 |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
3 | Supply and fixing, testing and commissioning of Slotted Pipe Oil Skimmer | No. | 1 |  |  | 0
| Size: To Suit 750mm Wide Oil & Grease Trap |  |  |  |  | 0
| Size of Slotted Pipe: 200mm Dia |  |  |  |  | 0
| Type of Operation: Manual Hand Wheel |  |  |  |  | 0
| MOC of All Wetted Parts : SS 304 |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
0
4 | PH METER :- supply and Fixing of PH meter PO 650 ph/orp with push button type for physical dimensions 105x105x130mm cut out size 92x92mm enclosure ABS weather proof IP-65 calibration /set point ,Sensor dimension 140mmx32mm ,Flow throw . It includeing cost and conveyance , all taxes specification Provided at the outlet of Sewerage treated water sump it including all taxes as directed by Engineer-in-charge . | No. | 1 |  |  | 0
5 | Supply and fixing, testing and commissioning of Coarse Bubble Diffusers | Nos. | 6 |  |  | 0
| Type: Disc Diffuser |  |  |  |  | 0
| Size: 80mm Dia |  |  |  |  | 0
| MOC: EPDM |  |  |  |  | 0
| Make: Rehau/OTT/SSI/Aquaflex/Techpro/Shridevi /Sreetech |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
6 | Supply and fixing, testing and commissioning of Equ Effluent/Sewage Pump | Nos. | 2 |  |  | 0
| Capacity of Pump: 4.00 Cu.m/Hr @ 6m Head |  |  |  |  | 0
| Type of Pump: Non Clog Vertical Submersible |  |  |  |  | 0
| Solid Handling Size: 10mm |  |  |  |  | 0
| Impeller Type: Non Clog |  |  |  |  | 0
| MOC of Casing: CI |  |  |  |  | 0
| MOC of Impeller: CI |  |  |  |  | 0
| Accessoreis: Auto Coupling, SS304 Lifting Chain, SS Guide Pipe, Control Panel with Level Switches for auto Start & Stop |  |  |  |  | 0
| Make: Kishor/KSB/Grundfos/CRI/Wilo/Kirloskar |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
7 | Supply and fixing, testing and commissioning of Mixer for Anoxic Tank | Nos. | 1 |  |  | 0
| Type: Turbine Type |  |  |  |  | 0
| RPM of Mixer: 50 |  |  |  |  | 0
| MOC of Shaft & Blades: SS 304 |  |  |  |  | 0
| Motor KW: 1.1 |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
8 | Supply and fixing, testing and commissioning of Aeration Blower | Nos. | 2 |  |  | 0
| Capacity of Blower: 120Nm3/Hr @ 5.5 MWC |  |  |  |  | 0
| Type of Blower: Twin Lobe |  |  |  |  | 0
| MOC of Blower: CI |  |  |  |  | 0
| Speed of Blower : Less than 1000 RPM |  |  |  |  | 0
| Speed of Blower Motor: 1440 RPM |  |  |  |  | 0
| The Blower shall be complete with Blower & Motor mounted on a common base frame, belt drive, belt guard, Suction & Discharge Silencer, Air Filter, Safety Valve, NRV, etc., complete. |  |  |  |  | 0
| Make: Kay/Everest/Swan |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
9 | Supply and fixing, testing and commissioning of Fine Bubble Diffusers | Nos. | 14 |  |  | 0
| Type: Tubular |  |  |  |  | 0
| Size: 1.0m Long x 90 Dia |  |  |  |  | 0
| MOC: EPDM |  |  |  |  | 0
| Make: Rehau/OTT/SSI/Aquaflex/Techpro/Shridevi/Sreetech |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
10 | Supply and fixing, testing and commissioning of Air Piping from Blower upto Diffusers for Equ Tank Blower & Aeration Blower | KGS | 100 |  |  | 0
| MOC of Exposed Pipes: SS 304 |  |  |  |  | 0
| MOC of Vertical Drops: SS 304 |  |  |  |  | 0
| MOC of Under Water pipes: SS 304 |  |  |  |  | 0
| MOC of Guide Pipe & Lifting Chain: SS 304 |  |  |  |  | 0
| The Air Piping shall be complete with Individual blower delivery piping with NRV, Diaphragm Valve, Main Header Piping from the Blower delivery up to equ tank/aeration tank including drop/vertical piping, header along the tank, vertical drop pipes with control valve & dismantling type joint, diffuser header pipe & laterals with nozzles for diffuser, end cap, vertical guide pipe at the other end of diffuser header, lifting chain, etc., complete. The design of piping shall be such that it should be possible to remove diffusers from the tanks without emptying tank & shutting off the system. The arrangement shall be that the we should be able to take out the Vertical drop pipe & the diffuser header just by dismantling the joint in the vertical drop pipe and should be able to refix the same in position. |  |  |  |  | 0
| Pipe Sizes: As per Diffuser Manufacturer recommendations. |  |  |  |  | 0
| The Contractor has to provide detailed air piping calc for the air pipes from the diffuser supplier to match the specified blower. |  |  |  |  | 0
| Battery Limit: Form Flange of Blowers till diffuser |  |  |  |  | 0
| The Piping cost is inclusive all necessary materials required for the piping like pipes, fittings, adopters, flanges, fasteners, pipe supports, clamps, valves, labour charges for fabrication, erection, pressure testing, etc., complete. |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
11 | Supply and fixing, testing and commissioning of Media for MBBR Tank | Cu.m | 8 |  |  | 0
| Volume of Media: 8 Cu.m |  |  |  |  | 0
| Shape of Media: Conical Frustum |  |  |  |  | 0
| Surface Area: 300 m2/m3 of media |  |  |  |  | 0
| Structure: Cylindrical with Fins |  |  |  |  | 0
| Sp Gravity: 0.9 to 0.95 |  |  |  |  | 0
| MOC: P P UV Stabilised (Black Colour ) (300 sqm area ,70000.00 Pieces per cum) |  |  |  |  | 0
| Make: MM Aqua/ Tecpro/Enery Equipment/Shridevi/Sreetech |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
12 | Supply and fixing, testing and commissioning of Internal Recirculation Pump | Nos. | 2 |  |  | 0
| Capacity of Pump: 1 Cu.m/Hr @ 5m Head |  |  |  |  | 0
| Type of Pump: Non Clog Vertical Submersible |  |  |  |  | 0
| Solid Handling Size: 10mm |  |  |  |  | 0
| Impeller Type: Non Clog |  |  |  |  | 0
| MOC of Casing: CI |  |  |  |  | 0
| MOC of Impeller: CI |  |  |  |  | 0
| Accessoreis: Auto Coupling, SS304 Lifting Chain, SS Guide Pipe, Control Panel with Level Switches for auto Start & Stop |  |  |  |  | 0
| Make: Kishor/KSB/Grundfos/CRI/Wilo/Kirloskar |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. Final payment after Lab Testing treated water satisfing the following parameters BOD less than 20, COD less than 50 |  |  |  |  | 0
13 | Supply and fixing, testing and commissioning of Sludge Pump | Nos. | 2 |  |  | 0
| Capacity of Pump : 1 Cu.m/Hr @ 5m Head |  |  |  |  | 0
| Type of Pump: Horizontal Centrifugal |  |  |  |  | 0
| Impeller Type: Non Clog |  |  |  |  | 0
| MOC of Casing: CI |  |  |  |  | 0
| MOC of Impeller: CI |  |  |  |  | 0
| Make: Johnson/Kirloskar/KSB/Kirloskar |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
14 | Supply and fixing, testing and commissioning of Filter Feed Pump | Nos. | 2 |  |  | 0
| Capacity of Pump: 5 Cu.m/Hr @ 20m Head |  |  |  |  | 0
| Type of Pump: Horizontal Centrifugal |  |  |  |  | 0
| Impeller Type: Closed |  |  |  |  | 0
| MOC of Casing: CI |  |  |  |  | 0
| MOC of Impeller: CI |  |  |  |  | 0
| Make: Johnson/Kirloskar/KSB/Kirloskar |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
15 | Supply and fixing, testing and commissioning of Pressure Sand Filter | No. | 1 |  |  | 0
| Capacity of Filter: 4.00 Cu.m/Hr. |  |  |  |  | 0
| Minimum Dia of Filter: 0.70m |  |  |  |  | 0
| Minimum HOS of Filter: 1.8m |  |  |  |  | 0
| Minimum Height of Filter Sand: 0.30m |  |  |  |  | 0
| Minimum Plate Thickness for Shell & Dish: 6mm |  |  |  |  | 0
| Type of Underdrain: Nozzle Plate with Plastic Nozzles |  |  |  |  | 0
| Type of Inlet: Inlet Distribution Box/ Bell Mouth. |  |  |  |  | 0
| Specification for Filter Media: As per CPHEEO Manual |  |  |  |  | 0
| MOC of Filter: MSEP |  |  |  |  | 0
| Accessories: Frontal Piping & Valves. |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
16 | Supply and fixing, testing and commissioning of Activated Carbon Filter | No. | 1 |  |  | 0
| Capacity of Filter: 4.00 Cu.m/Hr. |  |  |  |  | 0
| Minimum Dia of Filter: 0.70m |  |  |  |  | 0
| Minimum HOS of Filter: 1.8m |  |  |  |  | 0
| Minimum Height of Activated Carbon: 0.30m |  |  |  |  | 0
| Minimum Plate Thickness for Shell & Dish: 6mm |  |  |  |  | 0
| Type of Underdrain: Nozzle Plate with Plastic Nozzles |  |  |  |  | 0
| Type of Inlet: Inlet Distribution Box. |  |  |  |  | 0
| Type of Activated Carbon: Coal Based/Coconut shell |  |  |  |  | 0
| Minimum Iodine Value for Activated Carbon: 1000 |  |  |  |  | 0
| MOC of Filter: MSEP |  |  |  |  | 0
| Accessories: Frontal Piping & Valves. |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
17 | Supply and fixing, testing and commissioning of Hypochlorite solution dosing System | System | 1 |  |  | 0
| Dosing System shall be complete with |  |  |  |  | 0
| 1 No. - 20 Lit Capacity HDPE Tank with Inlet & Outlet Connections, Level Indicator |  |  |  |  | 0
| Dosing Pump, 0 - 5 LPH Capacity, 1Nos. |  |  |  |  | 0
| Complete Flexible Tubing with Valves, NRV's, Strainers, etc., from Dosing Tank to dosing Point |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
18 | Supply and fixing, testing and commissioning of Treated Water Pump | Nos. | 2 |  |  | 0
| Capacity of Pump: 5 Cu.m/Hr @ 20m Head |  |  |  |  | 0
| Type of Pump: Horizontal Centrifugal |  |  |  |  | 0
| Impeller Type: Closed |  |  |  |  | 0
| MOC of Casing: CI |  |  |  |  | 0
| MOC of Impeller: CI |  |  |  |  | 0
| Make: Johnson/Kirloskar/KSB/Grundfos |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
19 | Supply and fixing, testing and commissioning of Filter Press Feed Pump | Nos. | 2 |  |  | 0
| Capacity of Pump: 1 Cu.m/Hr @ 20m Head |  |  |  |  | 0
| Type of Pump: Screw Pump |  |  |  |  | 0
| Impeller Type: Screw |  |  |  |  | 0
| MOC of Casing: CI |  |  |  |  | 0
| MOC of stator : Nitrile |  |  |  |  | 0
| MOC of rotor : SS 304 |  |  |  |  | 0
| Make: PD pumps / Rotomac / Alpha helical /Roto |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
20 | Supply and fixing, testing and commissioning of Manual Plate Filter Press | No. | 1 |  |  | 0
| Size of Plate: 310 x 310mm |  |  |  |  | 0
| No. of Chambers: 4 Chamber |  |  |  |  | 0
| Operation: Hydraulic Pump |  |  |  |  | 0
| Capacity: For Dewatering of 0.5 Cu.m/Day, 3% Sludge in 10Hour |  |  |  |  | 0
| Make: Hydro Press/Yo-Tana/Amar |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
0
21 | Supply and fiing , testing and commissioning of Tube deck Media for Tube settler . | CUM | 2 |  |  | 0
| Settling Velocity 50 m/sec |  |  |  |  | 0
| Thickness 1.00 mm |  |  |  |  | 0
| Structure ; Chirvan V - type |  |  |  |  | 0
| Hopper slope : 55 degree to 0 degree |  |  |  |  | 0
| MOC : PVC |  |  |  |  | 0
| Make: Rehau/OTT/SSI/Aquaflex/Techpro/Shridevi/Sreetech |  |  |  |  | 0
| Sub - Total |  |  |  |  | 0
22 | Supply and fixing, testing and commissioning of Jib Crane for Lifting of Submersible Pumps | No. | 1 |  |  | 0
| Capacity : 0.5 Ton |  |  |  |  | 0
| Min Clear Height: 2.50m to the Bottom of the Hook (From Base plate). |  |  |  |  | 0
| Degree of Rotation: 360 Degrees. |  |  |  |  | 0
| Length of Boom: 2.0m to the Centre of Lifting Hook from the centre of mast. |  |  |  |  | 0
| Rotating Operation: Manual |  |  |  |  | 0
| Accessories Reqd: 0.5 Ton Capacity Chain Pulley Block with Lifting Chain of 9.0m + Trolley of reputed make. |  |  |  |  | 0
| Mast section: Circular Mast of required Height |  |  |  |  | 0
| Method of Installation: By Welding to Fish Plate embedded in concrete. |  |  |  |  | 0
| Make: Reputed |  |  |  |  | 0
| including all incidental and operational charges etc, as per approved drawings and as directed by Engineer-in-charge complete for finished item of work. |  |  |  |  | 0
| MAIN PANEL IN ELECTRICAL ROOM |  |  |  |  | 0
| APFC PANELS-100 KVAR |  |  |  |  | 0
22 | 250 A Aluminium Bus Bar with colour code. | No | 1 |  |  | 0
| Internal wiring with approved make cable |  |  |  |  | 0
| Earthing Flat: Providing suitable G.I Flat |  |  |  |  | 0
| Incommer: . |  |  |  |  | 0
| 250A Three Pole, MCCB of 36 KA of Makes: L&T / Schneider / Havells |  |  |  |  | 0
| Metering Set: |  |  |  |  | 0
| 0- 250A Digital Ammeter with selector switch . - 1 No. |  |  |  |  | 0
| 0-500V Digital Volt meter with selector switch - 1 No. |  |  |  |  | 0
| R, Y, B Indication lamps of LED type - 3 Nos. |  |  |  |  | 0
| 250/5A C.T coils - 3 Nos. |  |  |  |  | 0
| Auto/Manual selector switches for capacitors/Ammeter/ Voltmeter. - 8 No |  |  |  |  | 0
| 6-32A SP MCBs of Legrand/Schneider make - 6 No |  |  |  |  | 0
| 250A/5A CTs -3 Nos of kappa make or desired by field authority. |  |  |  |  | 0
| APFC relay 8 stage (makes: L&T / Neptune/ Schneider) |  |  |  |  | 0
| Outgoing: |  |  |  |  | 0
| 63 A TP, MCCB , 35/36 KA of Makes: L&T / Schneider / Havells - 5 No |  |  |  |  | 0
| 20 KVAR heavy duty capacitors of MPP - 5 Nos of Neptune / L&T/Schneider/ make |  |  |  |  | 0
| Capacitor duty contactors of L&T Make for 20 KVAR Capacitor, for 20 KVAR heavy duty capacitors - 5 No |  |  |  |  | 0
| 20 KVAR heavy duty capacitors of MPP - 5 Nos of L&T/Siemens/Schneider/EPCOS make |  |  |  |  | 0
| Capacitor duty contactors of L&T Make for 20 KVAR Capacitor, model No: MO C20 for 20 KVAR heavy duty capacitors - 5 No |  |  |  |  | 0
| Labour charges etc complete with connections for finished item of work including all accessories, Auto / Manual Selector switches, auxilary contactors for auto manual operation, CTs and push buttons, indication lamps for on and off indication with all accessories etc. compele for finished item of work. |  |  |  |  | 0
23 | Starter Panel | No | 1 |  |  | 0
| Incomer-1 : 160 Amps 25 KA TP MCCB | No | 1 |  |  | 0
| 160 A TPN Aluminum Rated Bus Bar |  |  |  |  | 0
| Outgoings: |  |  |  |  | 0
| 10 HP STAR Delta Starter with 13 - 18 A Rated MPCB & 3 No's 25 A Rated Contactor with Trip Contact & Add On Blocks | No | 2 |  |  | 0
| 7.5 HP STAR Delta Starter with 9 - 14 A Rated MPCB & 3 No's 12 A Rated Contactor with Trip Contact & Add On Blocks | No | 2 |  |  | 0
| 3 HP DOL Starter with 6 - 10 A Rated MPCB & 1 No's 9 A Rated Contactor with Trip Contact & Add On Blocks | No | 9 |  |  | 0
| 5 HP KW DOL Starter with 9 - 14 A Rated MPCB & 1 No's 12 A Rated Contactor with Trip Contact & Add On Blocks | No | 6 |  |  | 0
| Metering |  |  |  |  | 0
| 0-500 V Voltmeter | No | 1 |  |  | 0
| 0-160 A Ammeter | No | 1 |  |  | 0
| 160/5 CL's | No | 3 |  |  | 0
| Control MCB's | No | 3 |  |  | 0
| RYB Indication Lamps | Set | 1 |  |  | 0
24 | PIPING: |  |  |  |  | 0
24.1 | Supplying, Laying, Testing & Commissioning of complete piping for the 0.075 MLD E&STP to match the P & ID and to match the layout, using suitable material pipes of approved makes conforming to IS, including pipe specials like bends of suitable degree, elbow, tee, union/flanges, values, fasteners, Cutting the pipes to requirement, making joints with pipe specials, earth work excavation, laying, refilling as required, or in pipe supports including its foundation, pipe supports, clamping system, etc., Conducting wet run, rectifying the leaks if any in laid pipe work, etc, complete with valves as applicable. Battery Limits: From Head Manhole near the STP (Approx. 15m), piping for Treated Water Pump for a length of 100m from the STP boundary. The complete piping within the E&STP area shall be contractor's scope. |  |  |  |  | 0
| The Scope of Piping Shall Include the following: |  |  |  |  | 0
24.1.1 | Piping from Last Manhole to Coarse Screen Chamber - 200 Dia PVC 10 KSC Pipe | m | 10 |  |  | 0
24.1.2 | Delivery Piping with Valves & NRV for Raw Effluent/Sewage Pump up to Inlet Chamber - 80 NB - DI Pipe | m | 20 |  |  | 0
24.1.3 | Delivery Piping with Valves & NRV for Equ Effluent/Sewage Pump up to Anoxic Tank - 80 NB - uPVC Sch 40 Pipe | m | 12 |  |  | 0
24.1.4 | Delivery Piping with Valves & NRV for Internal Recirculation Pump up to Inlet of Anoxic Tank - 80 NB - uPVC Sch 40 Pipe | m | 15 |  |  | 0
24.1.5 | Piping from Sec Clarifier Launder Outlet to Filter Feed Tank through UV disinfection module - 80 NB uPVC Sch 40 Pipe | m | 5 |  |  | 0
24.1.6 | Filter Feed Pump Suction (Dual Suction, one from Filter Feed Tank & second from UF Feed Tank) and Delivery Piping with valves, NRV, up to frontal piping of PSF &ACF - 80 NB uPVC Sch 40 Pipe | m | 10 |  |  | 0
24.1.7 | Sludge Pump Suction and Delivery Piping with valves, NRV, up to Thickener/Inlet of Aeration Tank - 65 NB - uPVC Sch 40 Pipe | m | 10 |  |  | 0
24.1.8 | Treated Water Pump Suction and Delivery Piping with valves, NRV, up to battery limit - 80 NB - uPVC Sch 40 Pipe | m | 60 |  |  | 0
25.1 | SITC of DO Meter of approved make with interconnection wiring for auto switching on and off of Blowers, based on the DO Levels of the aeration tank. | No. | 1 |  |  | 0
25.1 | SITC of 50 Dia Electro Magnetic Flow Meter with local & remote indication panel with totaliser, including wiring between instrument & remote indicator, power supply wiring, etc., complete. | No. | 1 |  |  | 0
25.1 | Supply, installation, testing and commissioning of Bourdentype, stainless steel dial type pressure gauge withisolation valve and pipe having calibrationof 0-16 kg/cm2.MAKES: HGURU / FIEBIG and Approved makes | Nos | 15 |  |  | 0
25.1 | Supply and Installation of 600mm x 75mm x 2mm thick hot dip GIperforated cable tray with cover along with required angle supportswith coupler plates, Anchor bolts and nuts etc complete and the tray,should be fitted on the wall / Ceiling etc. complete. | RM | 20 |  |  | 0
0
| TOTAL C/O SUMMARY |  |  |  |  | 0

## Additional items
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for Additional items
Sl.No. | Description | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount
0
1 | [5 empty] | 0
2 | [5 empty] | 0
3 | [5 empty] | 0
4 | [5 empty] | 0
5 | [5 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| TOTAL C/O SUMMARY |  |  |  |  | 0