## Firefighting,FA & PA
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for Firefighting, Fire alarm, Public address and associated works
Sl No | DSR Code | Item Description | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount
I |  | INTERNAL HYDRANT SYSTEM
1 |  | Providing, laying, testing & Commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 including Weling, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipes on the wall/ceiling with suitable clamps/support frame and painting with two or more coats of synthetic enamel paint of required shade compete as required:
| 18.7.10 | 250 mm dia (wall thickness = 6.3 mm) | Rmt | 15 |  |  | 0
| 18.7.9 | 200 mm dia (wall thickness = 6.3 mm) | Rmt | 15 |  |  | 0
| 18.7.8 | 150 mm dia | Rmt | 789.6 |  |  | 0
| 18.7.7 | 100 mm dia | Rmt | 2649 |  |  | 0
| 18.7.6 | 80 mm dia | Rmt | 220 |  |  | 0
| 18.7.5 | 65 mm dia | Rmt | 708 |  |  | 0
| 18.7.4 | 50 mm dia | Rmt | 395 |  |  | 0
| 18.7.3 | 40 mm dia | Rmt | 347 |  |  | 0
| 18.7.2 | 32 mm dia | Rmt | 7913.5 |  |  | 0
| 18.7.1 | 25 mm dia | Rmt | 3538.16 |  |  | 0
0
2 | 18.10.1 | Supplying and fixing single headed Internal valve with Stainless steel couplings of 63mm dia instantaneous FM Gunmetal /stainless Steel coupling and cast iron wheel, ISI marked, confirming to IS 5930 (Type A) with blank Gumetal/Stainless steel cap and chain as required : Signle headed gunmetal Valve. | Each | 40 |  |  | 0
0
3 | 18.16.1 | Supplying and fixing 63 mm dia, 15 mtr long RRL hose pipe with 63 mm dia Male and Female couplings duly bound with GI wire, rivets etc conforming to IS 636 (Type -A) with Gunmetal. | Each | 96 |  |  | 0
0
4 | 18.17.1 | Supplying and fixing First -Aid Hose Reel with MS construction spray painted in Post office Red, Conforming to Is 884 with upto date amendments, complete with the following as required. 20.mm nominal internal dia water hose thermoplastic (Textile reinforced) type-2 as per IS : 12585, 20 mm nominal internal ida gun metal glove valve & nozzel. Drum and brackets for fixing the equipments on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S.Pipe and socket 30 Mtrs Hose Reel. | Each | 40 |  |  | 0
0
5 | TS SOR-23-24 ELEC-10.7.28 | Supplyand fixing of hose cabinet of size 750mm X 600mm x 250mm made of No 16 gauge SWG CRCA sheet with 6mm thick glazed glass door including necessary locking arrangement suitable to accommodate 2 Nos 15 mtr long Hose pipe, 1 No branch pipe, mounted on wall OR raised brick platform and duly painted with Post office red externally and white internally with synthetic enamel paint complete in all respect, for external hydrant as required. | Each | 48 |  |  | 0
0
6 | 18.18.1 | Supplying and fixing 63 mm dia gun metal short branch pies with 20 mm nominal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as require. | Each | 40 |  |  | 0
0
7 | 18.19.2 | Supplying and fixing of fire brigade connection of cast iorn body with gun metal male instantaneous inlet couplings complete with cap and chain as erqd. For suitable dia MS pipe connection confirming to IS 904 as required.- 4 Way -150 mm dia MS pipe. | Each | 1 |  |  | 0
II |  | SPRINKLER SYSTEM |  |  |  |  | 0
1 |  | Supplying, fixing, testing and commssioning of butterfly valve of PN 1.6 rating with bronze/gumetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required. |  |  |  |  | 0
| 18.11.8 | 250 mm dia | Each | QRO |  |  | 0
| 18.11.7 | 200 mm dia | Each | QRO |  |  | 0
| 18.11.6 | 150 mm dia | Each | 5 |  |  | 0
| 18.11.5 | 100 mm dia | Each | QRO |  |  | 0
| 18.11.4 | 80 mm dia | Each | QRO |  |  | 0
| 18.11.3 | 65 mm dia | Each | QRO |  |  | 0
| 18.11.2 | 50 mm dia | Each | 40 |  |  | 0
| 18.11.1 | 40 mm dia | Each | QRO |  |  | 0
| Maket Rate | 32 mm dia | Each | QRO |  |  | 0
| Maket Rate | 25 mm dia | Each | 80 |  |  | 0
0
2 | Maket Rate | Supply, Installation, Testing and Commissioning of 50 dia sight glass | Each | 40 |  |  | 0
0
3 | 16.8 | Providing and fixing in position the industrial type pressure gauges with gun metal / brass valves complete as required | Each | 46 |  |  | 0
0
4 | 18.22 | Providing & fixing of Pressure Switch in M.S Pipe line including connection etc., as required. | Each | 45 |  |  | 0
0
5 | 18.23.1 | Providing & fixing of Flow Switch in M.S Pipe line including connection etc., as required. 100 mm dia | Each | 45 |  |  | 0
0
6 | 18.24.2 | Providing, fixing, texting & commissioning of installation control valve of cast ior body, brass/ bronze working parts comprising of water motor alarm, bronze seat clapper, clapper arm and hydraulically driven mechanical gong bell to sound continious alarm whin the wet riser/sprinkler system activates, pressure gauges, emergecny release, stainer, pressure switch cock valve complete with drain valve bypass, test control box, ball valve, MS pipe of required size, flanges, orifice plate, ete of following size as required 100 mm dia. | Each | 40 |  |  | 0
0
7 | 18.21 | Providing, fixing, testing & commissioning of 15 mm dia quartzoid bulb type sprinklers of rating 68 degree centigrade with required accessories |  |  |  |  | 0
| 18.21.1 | Pendent Sprinler | Each | 2263 |  |  | 0
| 18.21.3 | Horizontal side wall sprinkler | Each | 270 |  |  | 0
0
8 | 18.25 | Supplying, installtion, testing & commissioning of sprinkler flexible pipe (UL listed) of stainless steel complete with 15 NPT on reducer thread with maximum working presure 175 PSI test pressure of 875 PS (Burst) with branch line (inlet) 25 mm NPT male thread to sprinkler head (Outlet) 15 mm NPt female thread with reducer, nipple, 2 side brackets, center brackt, stockbar of follwing sizes complete as required. |  |  |  |  | 0
| 18.25.2 | 1000 mm | Each | 155 |  |  | 0
| 18.25.3 | 1200 mm | Each | 155 |  |  | 0
0
9 | 18.29 | Providing, Installtion, testing & commissioning of adjustable rosette plate for 15mm dia in white finish UL Listen or FM approved compete as required. | Each | 310 |  |  | 0
0
10 | Market | Supply, delivery & Installaiton of Pipe Support for all types of pipes including hangars / fastners / elbows/supports / tees. | Kgs | 2800 |  |  | 0
0
11 | Market | Supply, Installation and Commissioning of Annunciator Panel with 64 Windows with Point, Zone & System Status used with RS 485 interface. | Each | 1 |  |  | 0
III |  | FIRE DITECTION AND ALARM SYSTEM |  |  |  |  | 0
1 | 17.2.1.1 | Supplying, installation, testing and commissioning of micro processor based intelligent addressable main fire alarm panel, central processing unit with the following 10 loop modules and capable of supporting not less than 240 devices (including detectors) and minimum 120 detectors per loop and loop length up to 2 km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 ± 5% V, 50 hz), 48 hrs back-up with 24 volt sealed maintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and facility to have seamless integration with analog/digital voice evacuation system (which is part of the schedule of work under SH: PA System) and shall be complete with all accessories . The panel shall be compatible for IBMS system with open protocol BACnet/ Modbus over IP complete as per for Ten Loop Panel | Set | 1 |  |  | 0
0
2 | 17.2.3 | Supplying, installation, testing & commissioning of repeater panel wih 320 character/ Touch screen LCD display with inbuilt reset, acknowledge and silence switches complete as required. | Each | 1 |  |  | 0
0
3 | 17.2.4 | Supplying, installation, testing & commissioning of intelligent analog addressable photothermal detector complete with mounting base complete as required. | Each | 508 |  |  | 0
0
4 | 17.2.15 | Supplying, installation, testing & commissioning of addressable horn cum strobe complete as required. | Each | 40 |  |  | 0
0
5 | 17.2.7 | Supplying, installation, testing & commissioning of fault isolator complete with base as required. | Each | 40 |  |  | 0
0
6 | 17.2.14 | Supplying, installation, testing & commissioning of addressable manual call point complete as required | Each | 40 |  |  | 0
0
7 | 17.2.5 | Supplying, installation, testing & commissioning of response indicator on surface/recessed MS Box having two LED, metallic cover complete with all connections etc as required | Each | 150 |  |  | 0
0
8 | TS SOR-23-24 ELEC-10.3.8 | Supply and installation of plug - in type rate of rise cum fixed temperature heat detectors including the cost of base plate. 75mm dia MS outlet box for fixing of the detector base, mounting accessories etc., complete as per specifications and as required. | Each | 20 |  |  | 0
0
9 | TS SOR-23-24 ELEC-10.3.6 | Supply and installation of plug - in type multi criterion detectors including the cost of base plate. 75mm dia M.S. outlet box for fixing of the detector base. Mounting accessories etc., complete as per specifications as required | Each | 130 |  |  | 0
0
10 | 17.5.2 | Supplying and drawing of cable Fire Retardant PVC insulated copper conductor cable in the existing surface / recessed steel conduit of following pairs, cores and size including connections and interconnections etc. as required. speaker cable Single pair, 2-core, 1.5 sqmm. | Rmt | 4000 |  |  | 0
0
11 | 1225 | Supplying and drawing of cable Fire Retardant PVC insulated copper conductor cable in the existing surface / recessed steel conduit of following pairs, cores and size including connections and interconnections etc, as required. | Rmt | 5000 |  |  | 0
IV |  | PUBLIC ADDRESING & EMERGENCY EVACUTION SYSTEM |  |  |  |  | 0
1 | 17.3.3 | Supplying, installation, testing & commissioning of 1.5/ 3 / 6W metal box ceiling/wall speakers complete as required | Each | 224 |  |  | 0
0
2 | 17.3.9 | Supplying, installation, testing & commissioning of Voice command keypad 6 zone, with microphone assembly complete as required | Each | 3 |  |  | 0
0
3 | Maket Rate | Supply, Installation, Testing and Commissioning of Amplifier 650 W for PA system suitable to operate on 230 V AC /12 V DC supply etc., complete.(AHUZA / OMEGA or equivalent) | Each | 2 |  |  | 0
0
4 | 17.5.3.1 | Supplying and fixing 25 mm dia MS flexible pipe with PVC coating along with all ancillaries and accessories like coupler etc. as required.speaker cable Single pair, 2-core, 1.5 sqmm | Rmt | 3000 |  |  | 0
0
5 | Maket Rate | 20 Zones Intelligent Public Address Center | Each | 1 |  |  | 0
0
6 | Maket Rate | Mixer PA System Racks Standing Cabinet | Each | 1 |  |  | 0
0
7 | TS SOR-23-24 ELEC-10.5.4 | Supply and fixing of Escape signage boards in Rigid Photo luminecent based glow in Dark rigid sheet with high intensity luminous properties with specificaiton of Cease Fire or its equivalent make Model-1ES01 | Each | 124 |  |  | 0
V |  | PORTABLE EXTINGUISHERS |  |  |  |  | 0
1 | TS SOR-23-24 ELEC-10.4.1 | ABC Powder type fire extinguisher of 6 Kgs. Capacity, with initial filling in brand new cylinder with powder coated finish, fitted with Gun metal union, high pressure gas cartridge, discharge hose, wall mounting bracket / stand etc. complete, confirming to IS:15683 (For car parking) | Each | 279 |  |  | 0
0
2 | TS SOR-23-24 ELEC-10.4.2 | Supply and fixing of Co2 4.5 Kg capacity type extinguisher with initial filling in brand new cylinder with powder coated finish, fitted with Gun metal union, high pressure, discharge hose, wall mounting bracket / stand etc. complete, confirming to IS:15683. electrical room | Each | 20 |  |  | 0
0
3 | TS SOR-23-24 ELEC-10.5.1 | Supply and fixing of 2 Kg Fire exitinguisher Clean Agent HCFC 123, Stored pressure type, IS 15683 : 2006 pressure guage, gross weight 3.7 Kg empty weight 1.7 Kg, can hight 344mm, Diameter 108mm, discharge time minimum 8 secs, controllable discharge mechanism, range minimum 2 meters, applicable on class A,B,C and electrically started Fire, A rating 1A, B rating 21B, can construction: Deep drawn & CO2 mig welded, Valve construction: Forging & Machining, Internal coating of Can: Epoxy powder coating, External coating of can: Epoxy polyster powder coating, sheet metal thickness: 1.60 mm, Helium leak detection tested, ISI & CE approved, 5 Years warranty. | Each | 20 |  |  | 0
0
4 | TS SOR-23-24 ELEC-10.4.5 | Supply and fixing of Water Mist type fire extinguisher 9 liters. Capacity, with initial filling in brand new cylinder with powder coated finish, fitted with Gun metal union, high pressure gas cartridge, discharge hose, wall mounting bracket / stand etc. complete, confirming to IS:15683. (Provided near Stair case landing) | Each | 68 |  |  | 0
VI |  | PUMPS AND PUMP ROOM |  |  |  |  | 0
1 | 18.1 | A) Supplying , installation , testing and commissioning of electric driven main fire pump suitable for automatic operation and consisting of following : complete in all respect as required. B) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520 C) Suitable HP Squirrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for operation on 415Volts, 3 phase 50 Hz. AC with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325 D) M.S. Fabricated common base plate, coupling, coupling guard, foundation bolts etc as required. E) Suitable cement concrete foundation duly plastered with anti vibration pads. 2850 lpm at 88 m Head | Set | 2 |  |  | 0
0
2 | 18.2 | (A) Supplying , installation, Testing and commissioning of diesel engine driven main fire pump suitable for automatic operation and consisting of following : complete in all respect as required : (Diesel Driven Pump) (B) Horizontal type, multistage, centrifugal pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal confirming to IS 150 (C) Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant IS standard complete with auto starting mechanism, 12 Volts / 24 Volts electric starting equipment, Diesel Tank, exhaust pipe extended upto 10 m. outside pump house duly insulated with 50 mm thick glass wool with 1.0mm thick alluminium sheet cladding, residential silencer, instruments and protection as per specification, stop solenoid for auto stop in the event of fault with audio indications, painted with post office red colour etc as required. (D) M.S. Fabricated common base plate, coupling, coupling guard, foundation bolts etc as required. (E) Suitable cement concrete foundation duly plastered with anti vibration pads. 2850 lpm at 88 m Head | Set | 1 |  |  | 0
0
3 | 18.3 | Supplying , installation , testing and commissioning of electric driven main fire pump suitable for automatic operation and consisting of following : complete in all respect as required : (Jockey Pump) (B) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical conforming to IS 1520. (C) Suitable HP SQ cage induction motor, TEFC type suitable for operation on 415Volts, 3 phase 50 Hz. AC with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325 (D) M.S. Fabricated common base plate, coupling, coupling guard, foundation bolts etc as required. (D) Suitable cement concrete foundation duly plastered with anti vibration pads. | Set | 2 |  |  | 0
0
4 | 18.5.3 | CONTROL PANELS: Fabrication, supply, Installtion testing & commissioning of Electrical Control panel of cubical construction, floor mounted type, fabricated out of 2 mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, poweder coated of approved shade after 7 tank treament process, calbe alley, inter-connection with suitable size copper conductor cable/soild copper strip, having swithgears and accessories, mountings and internal wireing, earth terminals, numbering etc., complete in all respect, sutable for amin fire pump, pressurisation pump & diesel pump set complete as per CPWD specification with following in coming and Outgoings, suitable for operation on 415V, 3 phase, 50Hz Ac Supply with enclosure protection class IP 42 as required. | Set | 1 |  |  | 0
|  | NCOMER: 250A, 50kA 4 Pole MCCB, Ics=100% Icu rating Digital Voltmeter 0-500V with selector switch Digital Ammeter (0-250 A) with selector swtich & CTs etc. LED type RYB phase indicating lamps, ON, OFF, trip indicating lamps Set of Copper Bus Bar 300A OUTGOING : ( Note : All outgoing feeders for pumps should have digital Ammeter with selector switches, and LED type ON, OFF, trip indicating lamps) Main Fire Pump: 125 A, 50kA TPN MCCB, Ics=100% Icu, with fully automatic Star/Delta starter suitable for 60 HP pump with overload protection, current sensing type single phase preventor complete with all acceessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. Jockey Pump:63 A, 50kA TPN MCCB, Ics=100% Icu, with suitable HP fully automatic Star/Delta starter with overload protection, current sensing type single phase preventor complete with all acceessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. DIESEL ENGINE CONTROL : Control for diesel engine comprising - Automatic/ Manual selctor switch & 3 attempts starting device, timers and relays as required, push buttons, start/stop in manual mode. Indicating lamp for high/ Low Lub. Oil pressure, High Water Temp and Engine on indication. Battery charger suitbale for 12V/24 V DC with boost and trickle selector switch, 0-30 V DC volt meter, and 0- 20 A DC Ammeter, All standard relays and accessories for automatic operation of diesel engine. |  |  |  |  | 0
0
5 | 18.2 | Supplying and fixing air vessle made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height with air reslease valve on top and flanged connection to riser, drain arrangemnt with 25 mm dia gun metal wheel valve with required accessories, pressure gauge and painting with syntheric enamel paint of approved shade as required. | Each | 1 |  |  | 0
0
6 | TS SOR-23-24 ELEC-10.7.41 | Supplying and fixing approved make 25 mm dia. With automatic air release valve with unions etc. complete. (PN 16) ( Spring loaded type) | Each | 7 |  |  | 0
0
7 | 18.15.5 | Providing, Installation, testing and commissioning of stainless steel Y-strainer fabricated out of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange with 250 mmm dia | Each | 2 |  |  | 0
0
8 | 18.12. | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required : |  |  |  |  | 0
| 18.7.10 | 250 mm dia | Rmt | 1 |  |  | 0
| 18.7.9 | 200 mm dia | Rmt | QRO |  |  | 0
| 18.7.8 | 150 mm dia | Rmt | 4 |  |  | 0
| 18.7.7 | 100 mm dia | Rmt | QRO |  |  | 0
| 18.12.4 | 80 mm dia | Rmt | 4 |  |  | 0
| 18.12.2 | 50 mm dia | Rmt | QRO |  |  | 0
0
9 |  | NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled / hot water circulation including insulation as specified. |  |  |  |  | 0
| 16.7.3.2 | 150 mm dia | Rmt | 5 |  |  | 0
| 16.7.3.4 | 100 mm dia | Rmt | QRO |  |  | 0
| 16.7.3.5 | 80 mm dia | Rmt | 2 |  |  | 0
0
10 |  | Flanged flexible joint: Supplying and fixing flanged flexible Joint to fire sump SI marked complete with nuts, bolts, washers, gaskets of following sizes as required : |  |  |  |  | 0
| Market | 150 mm dia | Rmt | 6 |  |  | 0
| Market | 80 mm dia | Rmt | 4 |  |  | 0
0
11 | TS SOR-23-24 ELEC-10.7.44 | Providing, fixing, testing & commissioning of installation control valve of cast iron body,brass/bronze working parts comprising of water motor alarm, bronze seat clapper, clapper arm and hydraulically driven mechanical gong bell to sound continuous alarm when the wet riser/sprinkler system activates, pressure gauges, emergency releases, strainer, pressure switch, cock valve complete with drain valve and bypass, test control box, ball valves, MS pipe of required size, flanges, orifice plate, gasket etc of follwing sizes as required 150 mm dia | Each | 2 |  |  | 0
0
12 | 9.2 | Supplying, making and laying of outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  | 0
| 9.2.23 | 3/4 X 150 sq. mm | Rmt | 30 |  |  | 0
| 9.2.21 | 3/4X 95 sq.mm | Rmt | 20 |  |  | 0
| 9.2.17 | 31/4X 25 sq.mm | Rmt | 20 |  |  | 0
| 9.2.5 | 3X16 sq.mm | Rmt | 20 |  |  | 0
0
13 | 1.17.1.k | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. 2x2.5 sq.mm | Rmt | 100 |  |  | 0
VII |  | EXTERNAL FIRE FIGHTING |  |  |  |  | 0
1 | 18.10.1 | Supplying and fixing Single headed external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Gunmetal/Stainless Steel coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal/Stainless Steel cap and chain as required : Single headed Gunmetal Valve | Each | 8 |  |  | 0
0
2 | 18.18.1 | Supplying and fixing 63 mm dia gun metal short branch pies with 20 mm nominal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as require: | Each | 8 |  |  | 0
0
3 | TS SOR-23-24 ELEC-10.7.43.c | Supplyand wrapping the anti corrosive material for buried pipes with coating of Primer and wrapping with 4 mm thick polymer corrosion resistant tape as per IS : 10221 with 15 mm overlap as per standard specificatios. 150 mm dia | Rmt | 309.6 |  |  | 0
0
4 | TS SOR-23-24 ELEC-9.4.28 | Providing floor mounting stand for keeping 4No of fire bucket 1500mm length, 900mm height made out of 40x40x6mm angle iron welded with 4 hooks and duly painted with one coat of red lead and two coats of enamel paint. | Each | 4 |  |  | 0
0
5 | Market rate | Supply,erection, testing and commisioning of Class B MS ERW pipe suitable for DG set cladded with 50mm thick mineral wool insulation covered with 24SWG Aluminium sheet and provided with rain cap as per specification inclusive of all supporting accessories of wall, ceiling 500mm dia. 5.15mm thick Exhaust Pipe for DG Motor Set | Rmt | 70 |  |  | 0
VIII |  | BASEMENT VENTILATION SYSTEM WITH AXIAL JET FAN |  |  |  |  | 0
1 | Market rate | Supply, Installation, Testing and commissioning of approved makes direct driven Smokespill Axial fans. Fan shall be balanced to vibration grade of G2.5 as per AMCA 204. Fan shall be complete with GSS casing ( 220 GSM ), Aluminium impeller, Imported make Motor Class H, special rated motor certified for 250 Deg C for 2 Hrs - 415/3P/50Hz. Complete Fan & motor assembly shall be Tested & certified for 250 Deg C for 2 Hrs. fire rating as per BS 7346 Part 2: 1990 Class B or EN 12101-3 by Third party Lab. Quoted price shall be including of fire redidant canvas connection, Mounting arrangement, Vibration isolater, Motorised damper, Starter panel, Suitable size of Armoured FRLS copper cabling with end termination with double compression gland and copper luges, Copper earthing, Suitable size of Shielded armoured FRLS Copper control cable up to PLC Panel with end termination with double compression gland and copper luges, suitable to interface with BMS & Fire Alarm System / PLC Panel, etc. complete as directed by the engineer-in-charge. The Starter Panel shall be proided with incomer MCCB, Bus Bar, Starters, control wiring,In bult Logic suitable to interface with BMS & Fire Alarm System / PLC Panel System as required for functioning of Smokespill Fan. The Panels shall be fabricated from 14 SWG MS sheet complete with required MS angle supports,tinned electrolytic copper bus bar chamber with required rating ,control switchgear and meter fixing plate, compartments for switch gear, meters and cables as per approved general arrangement plan , including 7 tank processes , approved shade powder coating, neoprene rubber gasket ,internal wiring required foundation , earthing terminal, detachable gland plate, required size. All electricals panel to be IP 54 protection and cables laid on G.I perforated trays. Complete installation to be Epoxy coated. 60835 cubic Feet per minute, 20 mmwg External Static Pressure, 950 rpm | Set | 8 |  |  | 0
0
2 | Market rate | Supply, Installation, Testing and commissioning of approved makes Induced Air Centrifugal Jet fans Fan shall be AMCA certified for Air & Sound performance, balanced to vibration grade of G2.5 as per AMCA 204. Fan shall be complete with GSS casing ( 220 GSM ), MS impeller, Imported make Dual speed smoke venting Class H, special rated motor certified for 250 Deg C for 2 Hrs - 415/3P/50Hz. Complete Fan & motor assembly shall be Tested & certified for 250 Deg C for 2 Hrs. fire rating as per BS 7346 Part 2: 1990 Class B or EN 12101-3 by Third party Lab. Quoted price shall be including of Mounting arrangement, Suitable size of Armoured FRLS copper cabling with end termination with double compression gland and copper luges up to PLC / starter Panel, Copper earthing, Copper earthing, suitable to interface with BMS & Fire Alarm System, etc. All electricals panel to be IP 54 protection and cables laid on G.I perforated trays. Complete installation to be Epoxy coated. The Locationing of the jet fans has to be done in such a way that the Air velocity at any point on the plane of 1m from the ground level should not be less than 0.25m/s during the normal mode. The CFD Analysis should be done for jet fan positioning by Original Equipment manufacturer. Centrifugal Type Jet fan (11100/5550 CMH, 97/24 Thrust force) Note : Qty. are indicative only. Actual Qyt. are base on CFD analysis. | Each | 16 |  |  | 0
0
3 | Market rate | Supply, installing, testing and commissioning of approved makes CO Sensor. Quoted price shall be including of Suitable size of Shielded armoured FRLS Copper control cable up to PLC Panel with end termination with double compression gland and copper luges, etc. complete all electricals panel to be IP 54 protection and cables laid on G.I perforated trays. Complete installation to be Epoxy coated. | Each | 26 |  |  | 0
0
4 | Market rate | Supplying, fabricating, installation, testing and commissioning free standing/Wall mounted type MS powder coated cubicle three phase, 415 V Electrical cum PLC panel. The Panel shall be proided with PLC Controller , incomer MCCB, Bus Bar, Starters, control wiring,In bult Logic suitable to interface with BMS & Fire Alarm System as required for functioning of jet fans /Main Exhaust Fan. The Panels shall be fabricated from 14 SWG MS sheet complete with required MS angle supports,tinned electrolytic copper bus bar chamber with required rating ,control switchgear and meter fixing plate, compartments for switch gear, meters and cables as per approved general arrangement plan , including 7 tank processes , approved shade powder coating, neoprene rubber gasket ,internal wiring required foundation , earthing terminal, detachable gland plate, required size. All electricals panel to be IP 54 protection and cables laid on G.I perforated trays. Complete installation to be Epoxy coated. Note : Co-relation of panel qty. to Qty. of Jet / Main Exh. & CO sensores shall be as per zoning and computational fluid dynamics (CFD) model . In case of Signal came from fire alarm System to PLC Panel to activate the fans in fire mode. | Each | 8 |  |  | 0
|  | Grand Total |  |  |  |  | 0

## Additional items
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for Additional items
Sl.No. | Description | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount
0
1 | [5 empty] | 0
2 | [5 empty] | 0
3 | [5 empty] | 0
4 | [5 empty] | 0
5 | [5 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| TOTAL C/O SUMMARY |  |  |  |  | 0