## HVAC
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for HVAC and associated works
Sl.No. | Description | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount
1 | Chiller, Cooling Tower & AHUs
1.1 | Supply, installation, testing and commissioning of Packaged roof top air cooled liquid chiller complete with multiple screw type compressors semi hermetic type, suction and discharge shut off valves, automatic safety control heater, automatic capacity control, condenser coils, fans, relief valve, flooded / DX type evaporators with closed cell elastomeric insulation, with multiple circuits, controls such as thermostatic expansion valve, Victaulic couplings, water flow switch, Integral refrigerant pipes & fittings, strainer, Sight glass, Isolating valves, suction piping and chiller, 25 mm dia chiller drain valve, insulation, first charge of gas and oil, base frames, vibration isolation springs, intergral wiring. Compressor sound attenuator, Guard for Condenser coil Accessories & microprocessor control panel with third party BAS Connectivity BACnet / Modbus RTU protocol The noise level not to exceed 80 dBA @ free field condition. Approved Eco Friendly Refrigerant R- 134 A |  |  |  |  | 0
1.1.1 | Chillers: Capacity: 300 TR, CHWI: 12ºC, CHWO: 7ºC. | Nos | QRO |  |  | 0
1.2 | COOLING TOWER :
1.2.1 | Design, Engineering, Procurements of materials of bought out components, Manufacturing, Assembly at shop, Testing, Painting packing, Supply, Transportation, Installation, Commissioning, performance testing at site & handing over of CTI Certified induced draft FRP tower of cross flow design with PVC fills. Uniform water & air distribution, integral cold water FRP basin with outlet suitable for gravity flow to cold water sump with vortex plate, fittings, fan, EFF-1 fan motor suitable for operation through VFD, fan motor drive, grouting pieces for basin like suction, make-up, quick fill, drain & over flow, ladder, etc. as per specifications. Motor should be suitable for 415 V, 3-Phase, 50 Hz. power supply. The Tower shall be installed on the terrace of Utility Block. The quoted price shall include the Insurance, Excise / Custom duty, CVD, VAT, Surcharge & Cess Custom clearance, inland transport from ICD to Bangalore site, shifting & installation in the Plant. | Set | QRO
Cooling Tower Capacity (TR) - Heat rejection of the condenser plus 10% extra
Water circulation rate - lps - 55
Cooling Tower Inlet Temp.-°C - 34.6
Cooling Tower Outlet Temp.-°C - 30.6
1.3 | DOUBLE SKIN AIR HANDLING UNITS:
Design, Engineering, Manufacturing, Testing, Painting, packing, Supply, Transportation, Installation, Commissioning, performance testing at site & handing over of all sheet metal medium pressure cabinet horizontal type double skinned (with 50 mm thick TF quality PUF insulation) with thermal breaks Air Handling Units complete fan section with supply air centrifugal backward curved (aerfoil design) fan, with fan motor suitable for VFD, belt drive, belt guard, vibration isolators, cooling coil section cooling coil, SS drain pan, filter section with Pre & Bag filter, Mixing Box. The AHU shall be of indoor mounted on pedestal. All sections & sandwich panels shall be fabricated, pressed and assembled at factory. AHU details will be as per Equipment Schedule and Specification. The quoted price shall include the Insurance, Excise / Custom duty, CVD, VAT, Surcharge & Cess Custom clearance, inland transport from ICD to Bangalore site, shifting & installation in the Plant.Fan outlet velocity not more than 9 m/s. Cooling coil pressure drop (water side) should not be more than 2 m.TR, total air, dehumidified air, cooling coil face area, number of rows of cooling coil, static pressure, fan motor KW and fan motor speed
1.3.1 | 50 TR, 4200 lps, 4200 lps, 1.7 Sqm., 6 rows, 65 mmwg, 5.5 KW & 1450 rpm | Set | 1
1.3.2 | 35 TR, 3000 lps, 3000 lps, 1.18 Sqm., 6 rows, 65 mmwg, 3.7 KW & 1450 rpm | Set | 1
1.3.3 | 18 TR, 1900 lps, 1900 lps, 0.76 Sqm., 6 rows, 65 mmwg, 3.7 KW & 1450 rpm | Set | 1
2 | CHILLED WATER PUMPS WITH INSULATION;- |  |  |  |  | 0
| Supply, Installation & Commissioning of horizontal end suction back pull out type pumps with bronze impeller and mechanical seal consisting of mounting frames, base frame, coupling, coupling guards, lubricating seal, motor etc. The pump motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC power supply. |  |  |  |  | 0
2.1 | CHWP Capacity: 1440 GPM for Chilled water recirculation | Nos | 2 |  |  | 0
3 | CHILLED WATER PIPING |  |  |  |  | 0
| Supply, installation, testing and commissioning of Chilled Water Piping with Insulation. All chilled water piping to be insulated with Nitrile Rubber Insulation. Where as outside piping shall be insulated with 18 kg/cum density TF quality expanded polystyrene pre-formed pipe sections with suitable thicknees as per specifications covered with chicken wire mesh and covered with Sand cement plaster. Piping will be complete with-ail MS Structure required for the installation of pipe and Pipe Support / Racks. |  |  |  |  | 0
3.1 | As per Specifications Supply & installation, testing and commissioning of MS ERW 'C class chilled water piping with insulation complete all as specified and directed for the following bore of pipes :- |  |  |  |  | 0
3.1.1 | 250 mm | Rmt | 80 |  |  | 0
3.1.2 | 200 mm | Rmt | 110 |  |  | 0
3.1.3 | 150 mm | Rmt | 60 |  |  | 0
3.1.4 | 125 mm | Rmt | 25 |  |  | 0
3.1.5 | 100 mm | Rmt | 25 |  |  | 0
3.1.6 | 80mm | Rmt | 250 |  |  | 0
3.1.7 | 65 mm | Rmt | 60 |  |  | 0
3.1.8 | 50 mm | Rmt | 220 |  |  | 0
3.1.9 | 40 mm | Rmt | 300 |  |  | 0
3.1.10 | 32 mm | Rmt | 150 |  |  | 0
3.1.11 | 25 mm | Rmt | 1650 |  |  | 0
3.2 | Supply, installation, testing and commissioning of insulating with Nitrile Rubber Insulation. Where as outside piping shall be insulated with fibre glass wool of density 48 kg/m3 & thickness 50 mm covered with chicken wire mesh and covered with Sand cement plaster complete all as specified and directed for the following size of valves :- |  |  |  |  | 0
3.2.1 | 250 mm | Rmt | 80 |  |  | 0
3.2.2 | 200 mm | Rmt | 110 |  |  | 0
3.2.3 | 150 mm | Rmt | 60 |  |  | 0
3.2.4 | 125 mm | Rmt | 25 |  |  | 0
3.2.5 | 100 mm | Rmt | 25 |  |  | 0
3.2.6 | 80mm | Rmt | 250 |  |  | 0
3.2.7 | 65 mm | Rmt | 60 |  |  | 0
3.2.8 | 50 mm | Rmt | 220 |  |  | 0
3.2.9 | 40 mm | Rmt | 300 |  |  | 0
3.2.10 | 32 mm | Rmt | 150 |  |  | 0
3.2.11 | 25 mm | Rmt | 1650 |  |  | 0
3.3 | Three Way Modulating Valve with actuator of the following dia :- |  |  |  |  | 0
3.3.1 | 25 mm | Nos | 285 |  |  | 0
3.4 | Balancing Valves (Extended Stem for 50 mm Insulation) of the following dia :- |  |  |  |  | 0
3.4.1 | 25 mm | Nos | 285 |  |  | 0
3.5 | Balancing & Control Valves (Extended Stem for 50 mm Insulation) of the following dia :- |  |  |  |  | 0
3.5.1 | 200 mm | Nos | 2 |  |  | 0
3.7 | Non Return valve |  |  |  |  | 0
3.7.1 | 200 mm | Nos | 4 |  |  | 0
3.8 | "Y" Strainers of the following dia :- |  |  |  |  | 0
3.8.1 | 200 mm | Nos | 4 |  |  | 0
3.8.5 | 25 mm | Nos | 285 |  |  | 0
3.9 | Butterfly valves of the following dia :- |  |  |  |  | 0
3.9.1 | 250 mm | Nos | 4 |  |  | 0
3.9.2 | 200 mm | Nos | 10 |  |  | 0
3.9.3 | 150mm | Nos | 4 |  |  | 0
3.9.4 | 125 mm | Nos | 2 |  |  | 0
3.9.5 | 100 mm | Nos | 2 |  |  | 0
3.9.6 | 80 mm | Nos | 285 |  |  | 0
3.1 | Flexible Connection |  |  |  |  | 0
3.10.1 | 200 mm | Nos | 4 |  |  | 0
3.11 | Ball Valve:(Extended Stem for 50 mm Insulation) of the following dia |  |  |  |  | 0
3.11.1 | 25 mm | Nos | 1425 |  |  | 0
3.12 | Drainn valve |  |  |  |  | 0
3.13 | 50 mm dia | Nos | 4 |  |  | 0
3.14 | 25 mm dia | Nos | 285 |  |  | 0
3.15 | Auto Airvent with Isolating Valve 25mm dia | Nos | 2 |  |  | 0
3.16 | Water Flow switch |  |  |  |  | 0
3.16.1 | 200 mm | Nos | 2 |  |  | 0
3.17 | Pressure Guage with ball valve | Nos |  |  |  | 0
3.18 | Thermo Meter | Nos |  |  |  | 0
3.19 | Pressurisation unit with necessary pumps, piping, valves, strainers, pressure guages, thermometers etc complete | Set | 1 |  |  | 0
3.2 | Expansion tank of required capacity with necessary piping, valves, straines etc complete | Nos | 1 |  |  | 0
3.21 | Makeup tank of required capacity with necessary piping, valves, straines etc complete | Nos | 1 |  |  | 0
3.22 | Air seperator of required capacity with necessary piping, valves, straines etc complete | Nos | 1 |  |  | 0
1 | Supply, Installation, Testing, Commissioning of Outdoor condensing unit comprising of Hermetic SCROLL compressor's, Heat Exchanger, propeller / axial fans, refrigerant Circuit, Safety Devices & Oil Recovery System and in built starter. The starter unit shall be operated both from local and remote Necessary Refrigerant Gas and oil charge.Compressor shall be equipped with inverter controller of Insulated Gate Bipolar Transistor (IGBT) type to be efficient & quiet. The outdoor unit shall have the multi-step of capacity control to meet load fluctuation and indoor unit individual control. Heat Exchanger shall be constructed with copper tubes mechanically bonded to aluminium fins to form a cross fin coil. Aluminium fins shall be covered by anti-corrosion resin film. Refrigerant shuold be R410A and COP should be 4.0 minimum. Unit shall have provision for BMS compatibility |  |  |  |  | 0
1.1 | 60 HP (20HP + 20HP + 20 HP) | Nos | 15 |  |  | 0
2 | VRV Indoor Cassette units |  |  |  |  | 0
| Supply, Installation,Testing & Commissioning of following capacity 4 way cassette VRV system Indoor unit along with cordedless remote, necessary supports, nuts & bolts etc complete. All units should be with inbuilt drain pump with minimum lift 750mm. Unit shall have provision for BMS compatibility |  |  |  |  | 0
2.1 | 1.6TR | Nos | 45 |  |  | 0
2.2 | 3.2 TR | Nos | 210 |  |  | 0
2.3 | 4.0 TR | Nos | 30 |  |  | 0
3 | Refrigerant Piping |  |  |  |  | 0
3.1 | Refrigerant Piping consisting of Suction line/liquide Piping & Fittings, with 19mm Armaflex"O" Insulation with finish as required, Refrigerant piping, interconnecting the liquid and suction lines between the VRV aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type 'K' with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. |  |  |  |  | 0
3.1.1 | Scope shall include complete clamping and claddling of cabling work and refrigerant piping, covered with PVC conduiting. | Rmt | 1200 |  |  | 0
3.1.2 | Communication Cabling between outdoor units / indoor units in 25 mm FRLS PVC Conduits, UV Stabilized as per manufacturer recommendation or CAT 6 4 pairs | Rmt | 1800 |  |  | 0
3.1.3 | Refrigerant Piping Joints as per drwgs and specs |  |  |  |  | 0
3.1.4 | For Suction Line | Nos | 300 |  |  | 0
| For Liquid Line | Nos | 300 |  |  | 0
4 | MS supports for ODU units |  |  |  |  | 0
4.1 | 60 HP | Nos | 1 |  |  | 0
5 | Providing PVC Drain Piping with 6mm Nitrile Rubber "O" Insulation with proper u trap etc |  |  |  |  | 0
5.1 | 25 MM dia drain pipe | Rmt. | 400 |  |  | 0
5.2 | 32 MM dia drain pipe | Rmt. | 1500 |  |  | 0
5.3 | 40 MM dia drain pipe | Rmt. | 250 |  |  | 0
6 | Supervision by specialist, Testing & Comisssioning including charge of R 410 - A Gas & Compressor Oil complete outdoor, Indoor Units and systems. | Lot | 1 |  |  | 0
| TOTAL C/O SUMMARY |  |  |  |  | 0

## Additional items
NAME OF PROJECT: Construction of Innovation Office Building (IOB) in Hyderabad
NATIONAL PAYMENTS CORPORATION OF INDIA (NPCI)
RFP # NPCI/2023-24/DC/036 dated 30.11.2023
Bill of Quantities for Additional items
Sl.No. | Description | Unit | Indicative Quantity | Bidders Quantity | Rate | Amount
0
1 | [5 empty] | 0
2 | [5 empty] | 0
3 | [5 empty] | 0
4 | [5 empty] | 0
5 | [5 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| TOTAL C/O SUMMARY |  |  |  |  | 0